## Slide 1: Installing a Physical Network
Chapter 5

## Slide 2: Objectives
Recognize and describe the functions of basic components in a structured cabling system
Explain the process of installing structured cable
Install a network interface card
Perform basic troubleshooting on a structured cable network

## Slide 3: Introduction (1 of 2)
Figure 5.1 What an orderly looking network!

## Slide 4: Introduction (2 of 2)
Figure 5.2 A real-world network

## Slide 5: Historical/Conceptual
Understanding Structured Cabling

## Slide 6: Structured Cabling
Telecommunications Industry Association/Electronic Industries Alliance (TIA/EIA) sets standards for structured cabling
Details on every aspect of cabled network
  Examples: type of cabling and position of wall outlets
  EIA ceased operations on February 11, 2011
Notes: Note (p. 89): EIA ceased operations in 2011, but various groups (like TIA) maintain the standards. Expect to see EIA on the CompTIA Network+ exam.

## Slide 7
What does Telecommunications Industry Association (TIA) mean?
The Telecommunications Industry Association (TIA) is a trade association which is accredited by the American National Standards Institute (ANSI) in order to develop industry standards for information and communication technologies (ICT) products such as cellular towers, data terminals, VoIP devices, satellites, telephone terminal equipment and many more. TIA has members from all over the industry and currently represents nearly 400 different companies.
TIA was a subdivision of EIA.

## Slide 8: The Goal of Structured Cabling
Create a safe, reliable cabling infrastructure
  Networks
  Telephone
  Video
  Anything that needs low-power, distributed cabling
Notes: Note (p. 90): A structured cabling system is useful for more than just computer networks. You’ll find structured cabling defining telephone networks and video conferencing setups, for example.
Tech Tip: Integrating Wi-Fi (p. 90)
Many networks today have a wireless component in addition to a wired infrastructure. The switches, servers, and workstations rely on wires for fast networking, but the wireless component supports workers on the move, such as salespeople. This chapter focuses on the wired infrastructure. Once we get through Wi-Fi in Chapter 14, “Wireless Networking,” I’ll add that component to our networking conversation.

## Slide 9: The Focus of This Chapter
Cable basics
Network components
Assessment of connections leading outside the network

## Slide 10: Cable Basics – A Star Is Born (1 of 2)
A typical physical star network
  A switch
  UTP cable
  A few PCs

## Slide 11: Cable Basics – A Star Is Born (2 of 2)
Figure 5.3 A switch connected by UTP cable
to two PCs

## Slide 12: Issues with Installation
Problems with locating a switch in the middle of office space
  Exposed cables are vulnerable to physical damage
    Tripping hazard
    Stepping on cables will cause failure over time
  Presence of other devices can create electrical interference
  Limits ability to make changes to network

## Slide 13: A Better Installation Design
Provides safety
Provides hardware to organize and protect cabling
Uses a cabling standard with flexibility to allow for growth
  TIA/EIA developed standards for cable installation
Notes: Cross Check: TIA/EIA Standards (p. 91)
You should remember the TIA/EIA 568 standards from Chapter 3, “Ethernet Basics,” but do you remember how to tell the difference between 568A and 568B? Why were the standards considered necessary?
Tech Tip: Professional Cabling Certifications with BICSI (p. 91)
Installing structured cabling properly takes a startlingly high degree of skill. Thousands of pitfalls await inexperienced network people who think they can install their own network cabling. Pulling cable requires expensive equipment, a lot of hands, and the ability to react to problems quickly. Network techs can cost employers a lot of money—not to mention losing their good jobs—by imagining they can do it themselves without the proper knowledge. If you are interested in learning more details about structured cabling, an organization called the Building Industry Consulting Service International (BICSI) (www.bicsi.org) provides a series of widely-recognized certifications for the cabling industry.

## Slide 14: Test Specific
Structured Cable Network Components

## Slide 15: Structured Cable Network Components (1 of 2)
Telecommunications room
  All cables concentrate in this one area
Horizontal Cabling [HC](a run)
Work area: office or cubicle

## Slide 16: Structured Cable Network Components (2 of 2)
Figure 5.4 Telecommunications room

## Slide 17: Horizontal Cabling (1 of 3)
Runs from telecommunications room to PCs
CAT 5e or better UTP
Solid core (better, but can break)
  Better conductor than stranded core
  Will break if mishandled
Stranded core (can withstand some bending)
  Not as good a conductor
  Stands up to handling without breaking
Notes: Exam Tip (p. 92): A single piece of cable that runs from a work area to a telecommunications room is called a run.

## Slide 18: Horizontal Cabling (2 of 3)
Figure 5.5 Horizontal cabling and work area

## Slide 19: Horizontal Cabling (3 of 3)
Figure 5.6 Solid and stranded core UTP
Solid Wires
Stranded
Wires

## Slide 20: TIA/EIA Specifications (1 of 2)
TIA/EIA specifies Horizontal Cabling should always be solid core
Horizontal cabling – number of strands
  Four-pair UTP assumed
  High-end telephone setups use 25- or 100-pair
Notes: Note (p. 93): Unlike previous CAT standards, TIA/EIA defines CAT 5e and later as four-pair-only cables.

## Slide 21: TIA/EIA Specifications (2 of 2)
Figure 5.7 25-pair UTP
Notes: Cross Check: Fire Ratings (p. 93)
You saw another aspect of cabling way back in Chapter 2, Cabling and Topology,” so check your memory here. What are fire ratings? When should you use plenum-grade cabling and when should you use riser-grade cabling? What about PVC? What are the differences?

## Slide 22: Choosing Your Horizontal Cabling
CAT 5e or CAT 6 UTP
CAT 6a for 10GBaseT
Install higher-rated cable for future technologies
Network installers may bid an installation using the lowest grade cable possible

## Slide 23: The Telecommunications Room
Heart of basic star
Intermediate distribution frame (IDF)
Endpoint of all horizontal runs from all work areas
Potentially messy place
  Organization is needed
Notes: Note (p. 93): The telecommunications room is also known as an intermediate distribution frame (IDF), as opposed to the main distribution frame (MDF), which we will discuss later in the chapter.

## Slide 24: Equipment Racks (1 of 4)
Central component: equipment racks
  All racks are 19 inches wide
Rack Height measured in Units (U)
  Most rack-mounted devices are 1U, 2U, or 4U
Types of racks
  Two post
  Four post
  Server rail rack
Notes: Note (p. 94): Equipment racks evolved out of the railroad signaling racks from the 19th century. The components in a rack today obviously differ a lot from railroad signaling, but the 19" width has remained the standard for well over 100 years.

## Slide 25: Equipment Racks (2 of 4)
Figure 5.8 A short equipment rack

## Slide 26: Equipment Racks (3 of 4)
Figure 5.9 A free-standing rack

## Slide 27: Equipment Racks (4 of 4)
Figure 5.10 A rack-mounted UPS
(Uninterruptible Power Supply)

## Slide 28: Patch Panels (1 of 6)
A box with a row of female (ports) in front
Permanent connections in back for connecting horizontal cables
  110 block
  Connect cables with punchdown tool
Proper labeling is crucial to organization of cables
Notes: The 110 block introduces less crosstalk than 66 blocks, so most modern installations of high-speed networks use it instead.

## Slide 29: Patch Panels (2 of 6)
Figure 5.11 Typical patch panels

## Slide 30: Patch Panels (3 of 6)
Figure 5.12 Punchdown tool

## Slide 31: Patch Panels (4 of 6)
Figure 5.13 Punching down a 110 block
Notes: Note (p. 95): Make sure you insert the wires according to the same standard (TIA/EIA 568A or TIA/EIA 568B) on both ends of the cable. If you don’t, you might end up swapping the sending and receiving wires (known as TX/RX reversed) and inadvertently creating a crossover cable.

## Slide 32: Patch Panels (5 of 6)
Figure 5.14 66-block patch panels
Notes: Exam Tip (p. 96): The CompTIA Network+ exam uses the terms 110 block and 66 block exclusively to describe the punchdown blocks common in telecommunication. In the field, in contrast, and in manuals and other literature, you’ll see the punchdown blocks referred to as 110-punchdown blocks and 66-punchdown blocks as well. Some manufacturers even split punchdown into two words, i.e., punch down. Be prepared to be nimble in the field, but expect 110 block and 66 block on the exam.

## Slide 33: Patch Panels (6 of 6)
Figure 5.15 Typical patch panels with labels
Notes: Tech Tip: Serious Labeling (p. 96)
The ANSI/TIA-606-C standard covers proper labeling and documentation of cabling, patch panels, and wall outlets. If you want to know how the pros label and document a structured cabling system (and you’ve got some cash to blow), check out the ANSI/TIA-606-C naming conventions from TIA.

## Slide 34: Patch Panel Configurations (1 of 2)
UTP, STP, or fiber ports
8, 12, 24, 48, or more ports
CAT rating
  CAT 6 or CAT 6a recommended
  Higher-rated panels support earlier standards

## Slide 35: Patch Panel Configurations (2 of 2)
Figure 5.16 CAT level on patch panel

## Slide 36: Patch Cables (1 of 3)
Connect the ports to the switch
Short (two to five feet)
Straight-through UTP cables
Stranded cable to tolerate more handling
Different colors facilitate organization
Most have reinforced (booted) connector

## Slide 37: Patch Cables (2 of 3)
Figure 5.17 Typical patch cable

## Slide 38: Patch Cables (3 of 3)
Figure 5.18 Network taking shape, with racks installed and horizontal cabling run
Notes: Exam Tip (p. 97): Some mission-critical networks require specialized electrical hardware. Although the CompTIA Network+ exam doesn’t refer to these boxes by name—rack mounted AC distribution boxes—it dances around some of the features. Notably, an AC distribution system can supply multiple dedicated AC circuits to handle any challenging setups.
If you install such a box in your rack, make sure to add labels to both systems and circuits. Proper system labeling and circuit labeling can make life much easier in the event of problems later on.

## Slide 39: The Work Area (1 of 4)
A wall outlet that serves as the termination point for horizontal cables
One or two female jacks to accept cabling
  CAT ratings
Mounting plate and faceplate components
PC connects to a wall outlet via a patch cable
Source of most network failures

## Slide 40: The Work Area (2 of 4)
Figure 5.19 Typical work area outlet

## Slide 41: The Work Area (3 of 4)
Connect the PC to the wall outlet
  Patch cable commonly used
  Patch cables add extra distance between the switch and the PC
    TIA/EIA specification allows only UTP cable lengths of 90 meters

## Slide 42: The Work Area (4 of 4)
Figure 5.20 Properly labeled outlet

## Slide 43: Structured Cable – Beyond the Star (1 of 2)
Cabling on one floor a single star topology
Cabling an entire building more complex
Most LANs connect to both Internet and telephone company
Notes: Note (p. 99): Structured cabling goes beyond a single building and even describes methods for interconnecting multiple buildings. The CompTIA Network+ certification exam does not cover interbuilding connections.

## Slide 44: Structured Cable – Beyond the Star (2 of 2)
Figure 5.21 25-pair UTP cables running to local 66-block

## Slide 45: Demarc and NIU (1 of 3)
Demarcation point (demarc)
  Refers to the physical location of the connection
  Marks the dividing line of responsibility for network function
Network interface unit (NIU)
  Serves as a demarc between a home network and ISP

## Slide 46: Demarc and NIU (2 of 3)
Figure 5.22 Typical home network interface box
Notes: Tech Tip: NIU=NIB=NID: Huh? (p. 100)
The terms used to describe the devices that often mark the demarcation point in a home or office get tossed about with wild abandon. Various manufacturers and technicians call them network interface units, network interface boxes, or network interface devices. (Some techs call them demarcs, just to muddy the waters further, but we won’t go there.) By name or by initial—NIU, NIB, or NID—it’s all the same thing, the box that marks the point where your responsibility begins on the inside.

## Slide 47: Demarc and NIU (3 of 3)
Figure 5.23 Typical office demarc
Notes: Note (p. 100): The best way to think of a demarc is in terms of responsibility. If something breaks on one side of the demarc, it’s your problem; on the other side, it’s the ISP/phone company’s problem.

## Slide 48: Connections Inside the Demarc (1 of 5)
Challenge to ISP/telephone provider
  The need to diagnose system faults
Smart jacks
  NIUs with remote loopback capability
Connections inside the demarc
  Network and telephone cables connect to customer-premises equipment (CPE)

## Slide 49: Connections Inside the Demarc (2 of 5)
Cabling that runs from the NIU to the CPE
Might be a multiplexer or a LAN switch connected to a patch panel
Main patch panel is called a vertical cross-connect

## Slide 50: Connections Inside the Demarc (3 of 5)
Figure 5.24 LAN vertical cross-connect

## Slide 51: Connections Inside the Demarc (4 of 5)
Figure 5.25 Telephone vertical cross-connect

## Slide 52: Connections Inside the Demarc (5 of 5)
The room that stores the demarc, telephone cross-connects, and LAN cross-connects
Different from individual telecommunications rooms that serve individual floors
Actual building and customer needs determine structured cabling system design

## Slide 53: Installing Structured Cabling

## Slide 54: Getting a Floor Plan (1 of 2)
Key to proper planning
Determine potential locations for telecommunications rooms
Locate physical firewalls
Gives an overall feel for the scope of the job
If no floor plan exists, create one

## Slide 55: Getting a Floor Plan (2 of 2)
Figure 5.26 Hand-drawn network floor plan

## Slide 56: Mapping the Runs (1 of 2)
Determine the length of cable runs
Determine the route of cable runs
Determine the location of each cable drop
Pricing
  Most network installers quote a per-drop cost
Raceway products allow cables to run outside the walls
Notes: Exam Tip (p. 103): Watch out for the word drop, as it has more than one meaning. A single run of cable from the telecommunications room to a wall outlet is often referred to as a “drop.” The word “drop” is also used to define a new run coming through a wall outlet that does not yet have a jack installed.

## Slide 57: Mapping the Runs (2 of 2)
Figure 5.27 A typical raceway

## Slide 58: Determining the Telecommunications Room Location (1 of 2)
Distance of no more than 90 meters from drops
Equipment power requirements
Humidity
Cooling
Access
Expandability

## Slide 59: Determining the Telecommunications Room Location (2 of 2)
Figure 5.28 An A/C duct cooling a telecommunications room

## Slide 60: Pulling Cable (1 of 9)
Requires two to three people
Start in telecommunications room and pull toward drops
Open drop ceiling and string via hooks or cable trays
Use correct tools
Hardest part: working around old cable installations in the ceiling

## Slide 61: Pulling Cable (2 of 9)
Figure 5.29 Cable trays over a drop ceiling

## Slide 62: Pulling Cable (3 of 9)
Figure 5.30 Messy cabling nightmare

## Slide 63: Pulling Cable (4 of 9)
Follow local codes, TIA/EIA, and NEC
Vertical drops require a lot of skill
Install a low-voltage mounting bracket to hold faceplate
Use cable guides to bring the cables down to the equipment rack

## Slide 64: Pulling Cable (5 of 9)
Figure 5.31 Nicely run cables
(image is vertical in the book)

## Slide 65: Pulling Cable (6 of 9)
Figure 5.32 Cutting a hole

## Slide 66: Pulling Cable (7 of 9)
Figure 5.33 Locating a dropped pull rope

## Slide 67: Pulling Cable (8 of 9)
Figure 5.34 Installing a mounting bracket

## Slide 68: Pulling Cable (9 of 9)
Figure 5.35 End of cables guided to rack

## Slide 69: Making Connections (1 of 2)
Connecting the work areas
  Crimp a wall jack to wire
  Mount the faceplate
  Fit the jack into the faceplate

## Slide 70: Making Connections (2 of 2)
Figure 5.36 Crimping a jack

## Slide 71: Rolling Your Own Patch Cables (1 of 7)
Use stranded UTP cable matching the CAT level of the horizontal runs
Use a special crimp for stranded cable
  RJ-45 crimper with built-in stripper
  Wire snips
  See step-by-step instructions and Figures 5.37 through 5.42 in the text

## Slide 72: Rolling Your Own Patch Cables (2 of 7)
Figure 5.37 Crimper and snips

## Slide 73: Rolling Your Own Patch Cables (3 of 7)
Figure 5.38 Properly stripped cable

## Slide 74: Rolling Your Own Patch Cables (4 of 7)
Figure 5.39 Inserting the individual strands

## Slide 75: Rolling Your Own Patch Cables (5 of 7)
Figure 5.40 Crimping the cable

## Slide 76: Rolling Your Own Patch Cables (6 of 7)
Figure 5.41 Properly crimped cable

## Slide 77: Rolling Your Own Patch Cables (7 of 7)
Figure 5.42 Adding a boot
Notes: Try This! Crimping Your Own Cable (p. 108)
If you’ve got some spare CAT 5 lying around (and what tech enthusiast doesn’t?) as well as a cable crimper and some crimps, go ahead and use the previous section as a guide and crimp your own cable. This skill is essential for any network technician. Remember, practice makes perfect!

## Slide 78: Connecting the Patch Panels (1 of 3)
Incorporate good cable management
Plastic D-rings guide patch cables neatly
Finger boxes guide individual cables
Organize to mirror the network layout
  Physical or logical layout
Document everything clearly and carefully

## Slide 79: Connecting the Patch Panels (2 of 3)
Figure 5.43 Bad cable management

## Slide 80: Connecting the Patch Panels (3 of 3)
Figure 5.44 Good cable management

## Slide 81: Testing the Cable Runs
Verify each cable run can handle the network speed
Testing tools
  Advanced tools cost $5,000 to $10,000
  Lower-end tools work for basic network testing
Notes: Note (p. 110): The test tools described here also enable you to diagnose network problems.

## Slide 82: Copper Challenges
Checking a potentially bad copper cable
  Examine length of the cable
  Look for broken or shorted wires
  Locate the point of the break
  Determine whether wires are terminated in the correct place
  Locate electrical or radio interference
  Test for crosstalk

## Slide 83: Tools to Use (1 of 5)
Cable tester
  Verifies cable and terminated ends are correct
  At the low-end: simple continuity testers
  Better testers run wiremap test to pick up shorts, crossed wires, and more
Continuity tester
  Multimeter
Notes: Note (p. 111): Many techs and network testing folks use the term wiremap to refer to the proper connectivity for wires, as in, “Hey Joe, check the wiremap!”

## Slide 84: Tools to Use (2 of 5)
Figure 5.45 Continuity tester

## Slide 85: Tools to Use (3 of 5)
Figure 5.46 Multimeter

## Slide 86: Tools to Use (4 of 5)
Time domain reflectometer (TDR)
  Medium-priced tester
  Tests continuity and wiremap
  Additional capabilities
    Determine length of cable and location of breaks
  Most come with loopback device

## Slide 87: Tools to Use (5 of 5)
Figure 5.47 A typical medium-priced TDR called a MicroScanner

## Slide 88: Crosstalk and Attenuation (1 of 5)
High-end testers can detect crosstalk and attenuation
Crosstalk
  Near-end crosstalk (NEXT) and far-end crosstalk (FEXT)
Attenuation
  Signal becomes steadily weaker as it progresses down the wire; more susceptible to crosstalk
Notes: Note (p. 112): Both NEXT and FEXT are measured in decibels (dB). See the Tech Tip below for the scoop.
Exam Tip (p.112):
Every network—copper or otherwise—experiences data loss or lag over distances and with enough traffic. Ethernet network frame traffic has latency, a delay between the time the sending machine sends a message and the time the receiving machine can start processing those frames. Add in a lot of machines and the network will also experience jitter, a delay in completing a transmission of all the frames in a message. This is perfectly normal and modern network technologies handle jitter fine. The only time it becomes a serious problem is in real-time voice communication. Excessive jitter generally sounds like, “Dude, you’re totally breaking up.” We’ll explore voice communication in Chapter 13, “Remote Connectivity,” in some detail.

## Slide 89: Crosstalk and Attenuation (2 of 5)
Figure 5.48 Crosstalk

## Slide 90: Crosstalk and Attenuation (3 of 5)
Figure 5.49 Near-end crosstalk

## Slide 91: Crosstalk and Attenuation (4 of 5)
Figure 5.50 Far-end crosstalk

## Slide 92: Crosstalk and Attenuation (5 of 5)
Figure 5.51 A typical cable certifier—a Microtest OMNIScanner (photo courtesy of Fluke Networks)
Notes: Tech Tip: Measuring Signal Loss (p. 113):
Signal loss in networking is measured in a unit called a decibel (dB). This applies to both electrical signals in copper wires and light signals in fiber cables. Unfortunately for a lot of network techs, a decibel is tough to grasp without a lot of math. I’m going to skip the technical details and give you a shorthand way to understand the numbers. When referring to a signal traveling from one end of a cable to another, you really care about how much information on that signal gets to the end, right? In a simple sense, if you have some interference, some imperfections in the cable or fiber, you’ll get some loss from beginning to end. Most people think about that loss in terms of percentage or even in more common terms, like “a little” or “a lot of” loss. No problem, right? The problem when you take that same concept to networking is that the percentages lost can be gigantic or really, really small. When you start talking about a 10,000% loss or a .00001% loss, most folks eyes glaze over. The numbers are simply too big or small to make intuitive sense. Technicians use the term decibel to describe those numbers in a more digestible format. When a tech looks at a signal loss of 3 dB, for example, he or she should be able to know that that number is a lot smaller than a signal loss of 10 dB.

## Slide 93: Fiber Challenges
Signal loss is important
  Measured in dB
  Causes can differ
Competing standards exist

## Slide 94: Signal Loss/Degradation (1 of 2)
Broken cables or open connections
Dirty connector
Connector mismatch in either cladding or core
Attenuation
Dispersion
Bend radius limitation
  Light leakage occurs with too much bend

## Slide 95: Signal Loss/Degradation (2 of 2)
Figure 5.52 Light leakage—note the colored glow at the bends but the dark cable at the straight

## Slide 96: Physical or Signal Mismatch (1 of 2)
Physical compatibility does not imply signal compatibility
  Must match single-mode or multi-mode fiber
  Different runs of fiber use different wavelength signals
Fiber technician must be highly skilled
  ST, SC, LC or other connector is very challenging

## Slide 97: Physical or Signal Mismatch (2 of 2)
Figure 5.53 Older fiber termination kit

## Slide 98: Optical Time Domain Reflectometer (OTDR) (1 of 2)
Determines continuity
Determines location of the break
Main issues with fiber
  Attenuation
  Light leakage
  Modal distortion

## Slide 99: Optical Time Domain Reflectometer (OTDR) (2 of 2)
Figure 5.54 An optical time domain reflectometer (photo courtesy of Fluke Networks)

## Slide 100: NICs

## Slide 101: Types of NICs (1 of 3)
Recognize different types of NICs by sight
Know how to install and troubleshoot NICs
Differences between UTP and fiber-optic NICs
  UTP Ethernet NICs use the RJ-45 connector
    Cable runs from the NIC to a switch
  Fiber-optic NICs
    Manufacturers use the same connector type for multiple standards

## Slide 102: Types of NICs (2 of 3)
Figure 5.55 Typical UTP NIC
Notes: Tech Tip: Onboard NICs (p. 115)
It’s a rare motherboard these days that doesn’t include an onboard NIC. This, of course, completely destroys the use of the acronym “NIC” for network interface card because no card is actually involved. But heck, we’re nerds and, just as we’ll probably never stop using the term “RJ-45” when the correct term is “8P8C,” we’ll keep using the term “NIC.” I know! Let’s just pretend it stands for network interface connection!

## Slide 103: Types of NICs (3 of 3)
Figure 5.56 Typical fiber NIC (photo courtesy of 3Com Corp.)

## Slide 104: Buying NICs
Recommend name-brand NICS, such as Intel
  Extra features
  Easy to replace missing driver
Recommend multispeed NICs
Stick with the same model for all systems
Notes: Note (p. 116): Many people order desktop PCs with NICs simply because they don’t take the time to ask if the system has a built-in NIC. Take a moment and ask about this!

## Slide 105: Physical Connections (1 of 2)
Physically install the NIC
Most PCs have built-in NICs

## Slide 106: Physical Connections (2 of 2)
Figure 5.57 PCI NIC

## Slide 107: Expansion Slots (1 of 3)
Peripheral Component Interconnect (PCI)
PCI Express (PCIe)
  One-lane or two-lane varieties
USB
  Convenient
  Carry one in the toolkit to test for a failed NIC

## Slide 108: Expansion Slots (2 of 3)
Figure 5.58 PCIe NIC

## Slide 109: Expansion Slots (3 of 3)
Figure 5.59 USB NIC

## Slide 110: Drivers
Insert the driver CD when prompted
OS likely has a preinstalled driver
  Using the CD offers additional features and utilities
Verify the driver install
  Windows: Device Manager
  Ubuntu Linux: Network applet
  macOS: Network utility in System Preferences

## Slide 111: Bonding
Link aggregation
  Doubles (or more) the speed between a machine and a switch
  Use identical NICs and switches from the same companies
Notes: Exam Tip (p. 117): The Link Aggregation Control Protocol (LACP) controls how multiple network devices send and receive data as a single connection.

## Slide 112: Link Lights (1 of 6)
UTP NICs have LEDs giving information about link state
  One to four link lights per card
  Lights give clues about what is happening
    Check the link lights first
    Tells you that the NIC is connected to a switch
  Switches also have link lights
  Multispeed devices have a link light that indicates speed

## Slide 113: Link Lights (2 of 6)
Figure 5.60 Mmmm, pretty lights!

## Slide 114: Link Lights (3 of 6)
Figure 5.61 Multispeed lights

## Slide 115: Link Lights (4 of 6)
Activity light
  Turns on when network traffic is detected
  Intermittently flickers when operating properly
Collision light
  Present on some older NICs
  Flickers when it detects collisions on the network
Fiber-optic NICs
  Many do not have lights

## Slide 116: Link Lights (5 of 6)
Figure 5.62 Link lights on a switch

## Slide 117: Link Lights (6 of 6)
Figure 5.63 Optical connection tester

## Slide 118: Diagnostics and Repair of Physical Cabling

## Slide 119: Diagnosing Physical Problems (1 of 3)
Try to eliminate software issues
  If one application fails, try another
Resolve hardware issues
  If all systems connected to one switch no longer see the network, the problem is likely the switch
Check your lights
  Have the user check connection status through link lights or software

## Slide 120: Diagnosing Physical Problems (2 of 3)
Figure 5.64 Disconnected NIC in Windows

## Slide 121: Diagnosing Physical Problems (3 of 3)
Check shared resources (servers)
Visually check cabling
Plug the system into a known good outlet
  If this works, suspect:
    Structured cabling running from the original outlet to the switch, or
    A bad connector
  Confirm with a continuity test

## Slide 122: Check the NIC (1 of 2)
Detect a bad NIC with an operating system utility
Use available NIC diagnostic software
Loopback test on NIC
  Internal only checks circuitry
  External (with loopback plug) tests the connecting pins
Notes: Note (p. 120): Onboard NICs on laptops are especially notorious for breaking due to constant plugging and unplugging. On some laptops, the NICs are easy to replace; others require a motherboard replacement.

## Slide 123: Check the NIC (2 of 2)
Figure 5.65 Loopback plug or adaptor

## Slide 124: Cable Testing (1 of 2)
Most problems occur at the work area
Test a cable run, including the patch cables
Check the coupler if one is used to extend a cable run

## Slide 125: Cable Testing (2 of 2)
Figure 5.66 Loopback plug in action

## Slide 126: Problems in the Telecommunications Room
Keep the diagnostic process organized and documented
Biggest concerns: power and environmental issues
Uninterrupted power supply (UPS)
  Is a battery backup that plugs into the wall
  Has built-in monitoring
  Enables orderly shutdown
Notes: Tech Tip: Online vs. Standby Power Supplies (p. 121)
You can purchase two different types of UPSs—online and standby. An online UPS continuously charges a battery that, in turn, powers the computer components. If the telecommunications room loses power, the computers stay powered up without missing a beat, at least until the battery runs out.
A standby power supply (SPS) also has a big battery but doesn’t power the computer unless the power goes out. Circuitry detects the power outage and immediately kicks on the battery.

## Slide 127: Monitoring Tools (1 of 2)
Voltage event recorder
  Plugs into a power outlet
  Tracks voltage over time
Environmental monitor
  Keeps a constant watch on humidity, temperature, and more
Notes: Note (p. 122): Using a high-quality UPS, installing temperature and environmental monitors; these fall into a much larger discussion called “managing risk.” Managing risk a big topic, so I’ve devoted the entire Chapter 18, Managing Risk,” to it.

## Slide 128: Monitoring Tools (2 of 2)
Figure 5.67 An excellent voltage event recorder (photo courtesy of Fluke Networks)

## Slide 129: Toners (1 of 3)
Device for tracing cables
Consists of a tone generator and a tone probe
Often referred to by brand-name “Fox and Hound”
Butt set
  Classic tool used by telephone repair technicians
Notes: Exam Tip (p. 122): You’ll see a tone probe referred to on the CompTIA Network+ exam as a toner probe.

## Slide 130: Toner (2 of 3)
Figure 5.68 Fox and Hound

## Slide 131: Toner (3 of 3)
Figure 5.69 Technician with a butt set
Notes: Another example of a tone probe